## EP-NAVADA PS
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: | [15 empty] | DOCUMENT NO | [5 empty] | DATE
TITLE: | [15 empty] | DESIGNED |  | CHECKED |  |  |  | SHEET
TITLE:
EARTHING DESIGN CALCULATIONS FOR NAVADA PS
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [10 empty] | : |  |  |  | Ohm-M |  |  | As per ERT Report
ii |  | Material of Earth Strip Selected | [10 empty] | :
iii |  | Type of Earth Electrode | [10 empty] | : |  |  | GI pipe & copper Plate |  |  |  |  | As per VOLUME: II C, Technical Specs.- 4.8 Earthing and Lightning protection system and Overall Layout
iv |  | Length of cu plate | [10 empty] | : |  |  | 0.6 | m
v |  | Width of cu plate | [10 empty] | : |  |  | 0.6 | m
vi |  | Total area of plate (on both sides) | [10 empty] | : |  |  | 0.72 | m2
vii |  | Length of pipe electrode, l | [10 empty] | : |  |  | 3 | m
viii |  | Dia. of pipe electrode, d | [10 empty] | : |  |  | 40 | NB
ix |  | No. of Earth Electrodes( Plate cum Pipe ), N | [10 empty] | : |  |  |  | Nos.
x |  | Length of Earth Grid Strip Considered, L | [10 empty] | : |  |  |  | m
xi |  | Maximum Fault Current, I | [10 empty] | : |  |  |  | kA |  |  |  | Highest Value Considered
xii |  | Duration of Fault Current, t | [10 empty] | : |  |  | 1 | sec
xiii |  | Volumetric Heat Capacity of Conductor Material, Qc | [10 empty] | : |  |  |  | J/0C mm3 |  |  |  | As per IS:3043-1987, Pg.no.30
xiv |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [10 empty] | : |  |  |  | 0C
xv |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [10 empty] | : | [5 empty] | Ohm
xvi |  | Intial temperature of the Conductor, θi | [10 empty] | : |  |  | 50 | 0C
xvii |  | Final temperature of the Conductor, θf | [10 empty] | : |  |  | 500 | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [16 empty] | {As per IS:3043-1987, Pg.no.29}
:
Where,
{As per IS:3043-1987, Pg.no.30}
[12 empty] | K |  | :
|  | Cross Sectional area required, S | [10 empty] | : |  |  |  |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [11 empty] | :
|  | Cross sectional area after including allowances | [11 empty] | : |  |  |  | Sq. mm
|  | Hence Selected Strip Size | [11 empty] | : |  |  |  | Sq. mm.
2 |  | RESISTANCE OF GI PLATE
|  | Resistance of Earth Electrode is Given by | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
[13 empty] | : |  |  |  | Ω
3 |  | RESISTANCE OF GI PIPE
|  | Resistance of Earth Electrode is Given by | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
[13 empty] | : |  |  |  | Ω
4 |  | RESISTANCE OF EARTH ELECTRODE (COMBINED PIPE & PLATE ELECTRODE )
Resistance of Combined pipe & plate electrode is given by
[13 empty] | : |  |  |  | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [10 empty] | : |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [10 empty] | : |  |  |  | Ω
6 |  | RESISTANCE OF EARTH STRIP | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
Resistance of Earth Strip is Given by
Where,
[12 empty] | t | : |  |  | Thickness of Earth Strip = 0.8 cm
[12 empty] | Rs | : |  |  |  | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[13 empty] | : |  |  |  | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [16 empty] | {As per Clause 10.3, Page No.27 of IS 3043-1987}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [10 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [10 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [10 empty] | : |  |  |  | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Plate Electrode
|  | Area of Plate Electrode | [10 empty] | : |  |  | 0.72 | m2
|  | Total Area of Plate Electrode | [10 empty] | : |  |  | 0 | m2
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [10 empty] | : |  |  | 0.37699 | m2
|  | Total Area of Pipe Electrode | [10 empty] | : |  |  | 0 | m2
Buried Earth Strip
|  | Earth Strip Length | [10 empty] | : |  |  | 0 | m
|  | Earth Strip Width | [10 empty] | : |  |  | 0.05 | m
|  | Earth Strip Height | [10 empty] | : |  |  | 0.008 | m
|  | Total Area of Earth Strip | [10 empty] | : |  |  | 0.0008 | m2
|  | Hence Total Area of the Earthing Network (a) | [10 empty] | : |  |  |  | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[7 empty] | Current Dissipation (I) | [5 empty] | : |  |  | Current Density (i) * Total Area (a)
|  | I | [10 empty] | : |  |  | (A) * (B)
|  | I | [10 empty] | : |  |  |  | kA
Maximum fault current dissipation of system is more than selected fault current of 31.5 kA. Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 31.5 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 65 x 10 mm G.I.
|  | 2. Total Earth Grid Resistance is | [8 empty] | 0 |  |  | Ω | which is less than 1 Ω.
|  | 3. Earth Electrode selected is . | [5 empty] | a) | 600mm x 600mm x 6 mm GI Plate for Transformer Body
[8 empty] | b) | 600 x 600 x 3.15 mm cu Plate for Transformer neutral, with 40 NB dia GI.Pipe.
As per VOLUME: II C, Technical Specs. E, M & I works, S. No.-4.8. EARTHING & LIGHTNING PROTECTION SYSTEM: Clause No. - 4.8.3( m & n )
4. Earth Electrodes:
|  |  | S. No. |  | Equipment | [5 empty] | Earth Electrode | [8 empty] | Qty
|  |  | A |  | 7.5 MVA (2 No.)
|  |  | 1 |  | Transformer body Earthing | [5 empty] | 600mm x 600mm x 6 mm GI Plate | [8 empty] | 2 Nos.
|  |  | 2 |  | Transformer neutral Earthing | [5 empty] | 600 x 600 x 3.15 mm cu Plate | [8 empty] | 2 Nos.
|  |  | B |  | 160 KVA (1 No.)
|  |  | 3 |  | Transformer body Earthing | [5 empty] | 600mm x 600mm x 6 mm GI Plate | [8 empty] | 2 Nos.
|  |  | 4 |  | Transformer neutral Earthing | [5 empty] | 600 x 600 x 3.15 mm cu Plate | [8 empty] | 2 Nos.
|  |  | 5 |  | Subatstaion & Main Earth Pits | [5 empty] | 600mm x 600mm x 6 mm GI Plate | [8 empty] | 3 Nos.
NAVADA (11 KV Switchyard)
[5 empty] | 1 | Earth Pit | [8 empty] | 4 Nos.
[5 empty] | 2 | Erath Strip | [8 empty] | 85 mtrs.
NAVADA (Pump house)
[5 empty] | 1 | Earth Pit | [8 empty] | 4 Nos.
[5 empty] | 2 | Erath Strip | [8 empty] | 530 mtrs.
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout (LE200907-E-WS-CW-DD-4011)
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_pl= ρ/4 √(/A)
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_𝑒= (𝑅_𝑝𝑙×𝑅_𝑝𝑖)/(𝑅_𝑝𝑙+𝑅_𝑝𝑖 )
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
C

## 12 (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | #REF! | [7 empty] | DOCUMENT NO | [8 empty] | DATE
[11 empty] | #REF! | [8 empty] | #REF!
TITLE: |  |  | #REF! | [7 empty] | DESIGNED |  |  |  | CHECKED |  |  |  |  | SHEET
TITLE: | [10 empty] | #REF! |  |  |  | #REF!
EARTHING DESIGN CALCULATIONS FOR BCWR-1
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [5 empty] | : |  |  | 100 |  |  | Ohm-M |  |  |  | Assumed |  |  | Silty clays type of soil
ii |  | Material of Earth Strip Selected | [5 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [5 empty] | : |  |  | GI pipe | [7 empty] | From GA Drawing and Overall Layout
iv |  | Length of pipe electrode, l | [5 empty] | : |  |  | 3 |  |  | m
v |  | Dia. of pipe electrode, d | [5 empty] | : |  |  | 40 |  |  | mm
vi |  | No. of Earth Electrodes( Plate cum Pipe ), N | [5 empty] | : |  |  | 11 |  |  | Nos.
vii |  | Length of Earth Grid Strip Considered, L | [5 empty] | : |  |  | 500 |  |  | m
viii |  | Maximum Fault Current, I | [5 empty] | : |  |  | 50 |  |  | kA
ix |  | Duration of Fault Current, t | [5 empty] | : |  |  | 1 |  |  | sec
x |  | Volumetric Heat Capacity of Conductor Material, Qc | [5 empty] | : |  |  | 0.0038 |  |  | J/0C mm3 |  |  |  |  | As per IS:3043-Reaffiremed in 2018
xi |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [5 empty] | : |  |  | 202 |  |  | 0C
xii |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [5 empty] | : |  |  | 0.000138 |  |  |  |  | Ohm
xiii |  | Intial temperature of the Conductor, θi | [5 empty] | : |  |  | 40 |  |  | 0C
xiv |  | Final temperature of the Conductor, θf | [5 empty] | : |  |  | 500 |  |  | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [13 empty] | {As per IS:3043-2018}
:
Where,
{As per IS:3043-2018}
[7 empty] | K |  | : |  | 80.69
|  | Cross Sectional area required, S | [5 empty] | : |  |  | 619.66 |  |  |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [6 empty] | : |  | No Allowance | [10 empty] | 20 x 3
|  | Cross sectional area after including allowances | [6 empty] | : |  | 619.66 |  |  |  | Sq. mm | [6 empty] | 25 x 3
25 x 6
|  | Hence Selected Strip Size | [6 empty] | : |  | 65 | X | 10 |  | Sq. mm. | [6 empty] | 25 x 8
32 x 6
32 x 10
3 |  | RESISTANCE OF GI PIPE | [19 empty] | 50 x 10
|  | Resistance of Earth Electrode is Given by | [12 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [6 empty] | 65 x 10
75 x 12
[8 empty] | = |  |  | 26.59 |  |  | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [5 empty] | = |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [5 empty] | = |  |  | 2.42 |  |  | Ω
6 |  | RESISTANCE OF EARTH STRIP | [12 empty] | {As per IS 3043-2018}
Resistance of Earth Strip is Given by
Where,
[7 empty] | t | : |  |  | Thickness of Earth Strip = 1.0 cm
[7 empty] | Rs | = |  |  | 0.38853 |  |  | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[7 empty] | RG | = |  |  | 0.33478 |  |  | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [13 empty] | {As per IS 3043-2018}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [5 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [5 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [5 empty] | = |  |  | 757 |  |  | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [5 empty] | : |  |  | 0.37699 |  |  | m2
|  | Total Area of Pipe Electrode | [5 empty] | : |  |  | 4.1469 |  |  | m2
Buried Earth Strip
|  | Earth Strip Length | [5 empty] | : |  |  | 500 |  |  | m
|  | Earth Strip Width | [5 empty] | : |  |  | 0.065 |  |  | m
|  | Earth Strip Height | [5 empty] | : |  |  | 0.01 |  |  | m
|  | Total Area of Earth Strip | [5 empty] | : |  |  | 75.0013 |  |  | m2
|  | Hence Total Area of the Earthing Network (a) | [5 empty] | : |  |  | 79.1482 |  |  | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[5 empty] | Current Dissipation (I) |  |  | : |  |  | Current Density (i) * Total Area (a)
|  | I | [5 empty] | : |  |  | (A) * (B)
|  | I | [5 empty] | : |  |  | 59.9152 |  |  | kA
Maximum fault current dissipation of system is more than selected fault current of 50 kA . Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 50 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 65 x 10 mm G.I.
2. Earth Electrode selected is 40 mm dia GI. Pipe with 300 cm long
|  | 3. Total Earth Grid Resistance is |  |  |  | 0.33478 |  |  | Ω | which is less than 1 Ω.
4. Earth Electrodes:
a) For 2 Nos Transformer body Earthing - 3 Nos
b) For 2 Nos. Transformer neutral Earthing - 3 Nos
c) For Main Earth Pit -4 Nos
d) For Body Earth Pit - 4 Nos
e) For Subatstaion Earth Pits -3 Nos
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout.
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K

## 13 (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | #REF! | [7 empty] | DOCUMENT NO | [8 empty] | DATE
[11 empty] | #REF! | [8 empty] | #REF!
TITLE: |  |  | #REF! | [7 empty] | DESIGNED |  |  |  | CHECKED |  |  |  |  | SHEET
TITLE: | [10 empty] | #REF! |  |  |  | #REF!
EARTHING DESIGN CALCULATIONS FOR CWPH & WTP (AUL BLOCK)
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [5 empty] | : |  |  | 100 |  |  | Ohm-M |  |  |  | Assumed |  |  | Silty clays type of soil
ii |  | Material of Earth Strip Selected | [5 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [5 empty] | : |  |  | GI pipe | [7 empty] | From GA Drawing and Overall Layout
iv |  | Length of pipe electrode, l | [5 empty] | : |  |  | 3 |  |  | m
v |  | Dia. of pipe electrode, d | [5 empty] | : |  |  | 40 |  |  | mm
vi |  | No. of Earth Electrodes( Plate cum Pipe ), N | [5 empty] | : |  |  | 14 |  |  | Nos.
vii |  | Length of Earth Grid Strip Considered, L | [5 empty] | : |  |  | 500 |  |  | m
viii |  | Maximum Fault Current, I | [5 empty] | : |  |  | 50 |  |  | kA
ix |  | Duration of Fault Current, t | [5 empty] | : |  |  | 1 |  |  | sec
x |  | Volumetric Heat Capacity of Conductor Material, Qc | [5 empty] | : |  |  | 0.0038 |  |  | J/0C mm3 |  |  |  |  | As per IS:3043-Reaffiremed in 2018
xi |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [5 empty] | : |  |  | 202 |  |  | 0C
xii |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [5 empty] | : |  |  | 0.000138 |  |  |  |  | Ohm
xiii |  | Intial temperature of the Conductor, θi | [5 empty] | : |  |  | 40 |  |  | 0C
xiv |  | Final temperature of the Conductor, θf | [5 empty] | : |  |  | 500 |  |  | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [13 empty] | {As per IS:3043-2018}
:
Where,
{As per IS:3043-2018}
[7 empty] | K |  | : |  | 80.69
|  | Cross Sectional area required, S | [5 empty] | : |  |  | 619.66 |  |  |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [6 empty] | : |  | No Allowance | [10 empty] | 20 x 3
|  | Cross sectional area after including allowances | [6 empty] | : |  | 619.66 |  |  |  | Sq. mm | [6 empty] | 25 x 3
25 x 6
|  | Hence Selected Strip Size | [6 empty] | : |  | 65 | X | 10 |  | Sq. mm. | [6 empty] | 25 x 8
32 x 6
32 x 10
3 |  | RESISTANCE OF GI PIPE | [19 empty] | 50 x 10
|  | Resistance of Earth Electrode is Given by | [12 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [6 empty] | 65 x 10
75 x 12
[8 empty] | = |  |  | 26.59 |  |  | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [5 empty] | = |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [5 empty] | = |  |  | 1.9 |  |  | Ω
6 |  | RESISTANCE OF EARTH STRIP | [12 empty] | {As per IS 3043-2018}
Resistance of Earth Strip is Given by
Where,
[7 empty] | t | : |  |  | Thickness of Earth Strip = 1.0 cm
[7 empty] | Rs | = |  |  | 0.38853 |  |  | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[7 empty] | RG | = |  |  | 0.32257 |  |  | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [13 empty] | {As per IS 3043-2018}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [5 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [5 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [5 empty] | = |  |  | 757 |  |  | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [5 empty] | : |  |  | 0.37699 |  |  | m2
|  | Total Area of Pipe Electrode | [5 empty] | : |  |  | 5.2779 |  |  | m2
Buried Earth Strip
|  | Earth Strip Length | [5 empty] | : |  |  | 500 |  |  | m
|  | Earth Strip Width | [5 empty] | : |  |  | 0.065 |  |  | m
|  | Earth Strip Height | [5 empty] | : |  |  | 0.01 |  |  | m
|  | Total Area of Earth Strip | [5 empty] | : |  |  | 75.0013 |  |  | m2
|  | Hence Total Area of the Earthing Network (a) | [5 empty] | : |  |  | 80.2792 |  |  | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[5 empty] | Current Dissipation (I) |  |  | : |  |  | Current Density (i) * Total Area (a)
|  | I | [5 empty] | : |  |  | (A) * (B)
|  | I | [5 empty] | : |  |  | 60.7713 |  |  | kA
Maximum fault current dissipation of system is more than selected fault current of 50 kA . Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 50 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 65 x 10 mm G.I.
2. Earth Electrode selected is 40 mm dia GI. Pipe with 300 cm long
|  | 3. Total Earth Grid Resistance is |  |  |  | 0.32257 |  |  | Ω | which is less than 1 Ω.
4. Earth Electrodes:
a) For 2 Nos Transformer body Earthing - 3 Nos
b) For 2 Nos. Transformer neutral Earthing - 3 Nos
c) For Main Earth Pit -4 Nos
d) For Body Earth Pit - 4 Nos
e) For Subatstaion Earth Pits -3 Nos
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout.
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K

## REF (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | CONSTRUCTION OF (1) SILAUTA-MUSTAKIL GROUP OF VILLAGES WATER SUPPLY SCHEME & (2) CHANDI- BANGAR GROUP OF VILLAGES WATER SUPPLY SCHEME, DISTRICT - CHITRAKOOT(SURFACE WATER) | [7 empty] | DOCUMENT NO | [6 empty] | DATE
[11 empty] | LE200815-E-WS-CW-DC-4051 | [6 empty] | 10.03.21
TITLE: |  |  | ELECTRICAL EARTHING & LIGHTNING CALCULATIONS FOR IBPS - 1 TO 9, 11 (CHANDI BANGAR) | [7 empty] | DESIGNED |  | CHECKED |  |  |  |  | SHEET
TITLE: | [10 empty] | MR |  | VKT
EARTHING DESIGN CALCULATIONS FOR IBPS-2
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [5 empty] | : |  |  | 60 | Ohm-M |  |  |  | Assumed
ii |  | Material of Earth Strip Selected | [5 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [5 empty] | : |  |  | GI pipe & copper Plate | [5 empty] | From GA Drawing and Overall Layout
iv |  | Length of cu plate | [5 empty] | : |  |  | 0.6 | m
v |  | Width of cu plate | [5 empty] | : |  |  | 0.6 | m
vi |  | Total area of plate (on both sides) | [5 empty] | : |  |  | 0.72 | m2
vii |  | Length of pipe electrode, l | [5 empty] | : |  |  | 3 | m
viii |  | Dia. of pipe electrode, d | [5 empty] | : |  |  | 20 | mm
ix |  | No. of Earth Electrodes( Plate cum Pipe ), N | [5 empty] | : |  |  | 3 | Nos.
x |  | Length of Earth Grid Strip Considered, L | [5 empty] | : |  |  | 300 | m
xi |  | Maximum Fault Current, I | [5 empty] | : |  |  | 35 | kA
xii |  | Duration of Fault Current, t | [5 empty] | : |  |  | 1 | sec
xiii |  | Volumetric Heat Capacity of Conductor Material, Qc | [5 empty] | : |  |  | 0.0038 | J/0C mm3 |  |  |  |  | As per IS:3043-1987, Pg.no.30
xiv |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [5 empty] | : |  |  | 202 | 0C
xv |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [5 empty] | : |  |  | 0.000138 |  |  | Ohm
xvi |  | Intial temperature of the Conductor, θi | [5 empty] | : |  |  | 40 | 0C
xvii |  | Final temperature of the Conductor, θf | [5 empty] | : |  |  | 500 | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [11 empty] | {As per IS:3043-1987, Pg.no.29}
:
Where,
{As per IS:3043-1987, Pg.no.30}
[7 empty] | K |  | : |  | 80.69
|  | Cross Sectional area required, S | [5 empty] | : |  |  | 433.76 |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [6 empty] | : |  | 15
|  | Cross sectional area after including allowances | [6 empty] | : |  | 498.824 |  | Sq. mm
|  | Hence Selected Strip Size | [6 empty] | : |  | 50 x 10 |  | Sq. mm.
20 x 3
2 |  | RESISTANCE OF GI PLATE | [16 empty] | 25 x 3
|  | Resistance of Earth Electrode is Given by | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [5 empty] | 25 x 6
25 x 8
32 x 6
[8 empty] | : |  |  | 31.3329 | Ω | [6 empty] | 32 x 8
3 |  | RESISTANCE OF GI PIPE | [16 empty] | 32 x 10
|  | Resistance of Earth Electrode is Given by | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [5 empty] | 40 x 6
40 x 8
40 x 10
[8 empty] | : |  |  | 18.16 | Ω | [6 empty] | 50 x 6
50 x 8
4 |  | RESISTANCE OF EARTH ELECTRODE (COMBINED PIPE & PLATE ELECTRODE ) | [16 empty] | 50 x 10
65 x 10
|  |  | Resistance of Combined pipe & plate electrode is given by | [15 empty] | 75 x 12
[8 empty] | : |  |  | 11.5 | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [5 empty] | : |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [5 empty] | : |  |  | 3.84 | Ω
6 |  | RESISTANCE OF EARTH STRIP | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
Resistance of Earth Strip is Given by
Where,
[7 empty] | t | : |  |  | Thickness of Earth Strip = 0.8 cm
[7 empty] | Rs | : |  |  | 0.37937 | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[8 empty] | : |  |  | 0.34526 | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [11 empty] | {As per Clause 10.3, Page No.27 of IS 3043-1987}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [5 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [5 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [5 empty] | : |  |  | 977.2828 | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Plate Electrode
|  | Area of Plate Electrode | [5 empty] | : |  |  | 0.72 | m2
|  | Total Area of Plate Electrode | [5 empty] | : |  |  | 2.16 | m2
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [5 empty] | : |  |  | 0.1885 | m2
|  | Total Area of Pipe Electrode | [5 empty] | : |  |  | 0.56549 | m2
Buried Earth Strip
|  | Earth Strip Length | [5 empty] | : |  |  | 300 | m
|  | Earth Strip Width | [5 empty] | : |  |  | 0.05 | m
|  | Earth Strip Height | [5 empty] | : |  |  | 0.008 | m
|  | Total Area of Earth Strip | [5 empty] | : |  |  | 34.8008 | m2
|  | Hence Total Area of the Earthing Network (a) | [5 empty] | : |  |  | 37.5263 | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[5 empty] | Current Dissipation (I) |  |  | : |  |  | Current Density (i) * Total Area (a)
|  | I | [5 empty] | : |  |  | (A) * (B)
|  | I | [5 empty] | : |  |  | 36.6738 | kA
Maximum fault current dissipation of system is more than selected fault current of 35 kA. Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 35 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 50 x 10 mm G.I.
2. Earth Electrode selected is 600 x 600 x 3 mm cu. Plate with 20 mm dia GI. Pipe.
|  | 3. Total Earth Grid Resistance is |  |  |  | 0.34526 |  |  | Ω | which is less than 1 Ω.
4. Earth Electrodes:
a) For 1 Nos Transformer body Earthing - 2 Nos
b) For 1 Nos. Transformer neutral Earthing - 2 Nos
c) For 1 Nos. DG body Earthing - 2 Nos.
d) For 1 Nos. DG neutral Earthing - 2 Nos.
e) For Subatstaion & Main Earth Pits -3 Nos
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout (LE200815-E-WS-CW-DD-4057)
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_pl= ρ/4 √(/A)
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_𝑒= (𝑅_𝑝𝑙×𝑅_𝑝𝑖)/(𝑅_𝑝𝑙+𝑅_𝑝𝑖 )
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K

## 1 (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | #REF! | [7 empty] | DOCUMENT NO | [8 empty] | DATE
[11 empty] | #REF! | [8 empty] | #REF!
TITLE: |  |  | #REF! | [7 empty] | DESIGNED |  |  |  | CHECKED |  |  |  |  | SHEET
TITLE: | [10 empty] | #REF! |  |  |  | #REF!
EARTHING DESIGN CALCULATIONS FOR CWPH-WTP (AUL BLOCK)
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [5 empty] | : |  |  | 70 |  |  | Ohm-M |  |  |  | Assumed |  |  | Silty clays type of soil
ii |  | Material of Earth Strip Selected | [5 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [5 empty] | : |  |  | GI pipe | [7 empty] | From GA Drawing and Overall Layout
iv |  | Length of pipe electrode, l | [5 empty] | : |  |  | 3 |  |  | m
v |  | Dia. of pipe electrode, d | [5 empty] | : |  |  | 40 |  |  | mm
vi |  | No. of Earth Electrodes( Plate cum Pipe ), N | [5 empty] | : |  |  | 16 |  |  | Nos.
vii |  | Length of Earth Grid Strip Considered, L | [5 empty] | : |  |  | 300 |  |  | m
viii |  | Maximum Fault Current, I | [5 empty] | : |  |  | 50 |  |  | kA
ix |  | Duration of Fault Current, t | [5 empty] | : |  |  | 1 |  |  | sec
x |  | Volumetric Heat Capacity of Conductor Material, Qc | [5 empty] | : |  |  | 0.0038 |  |  | J/0C mm3 |  |  |  |  | As per IS:3043-Reaffiremed in 2018
xi |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [5 empty] | : |  |  | 202 |  |  | 0C
xii |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [5 empty] | : |  |  | 0.000138 |  |  |  |  | Ohm
xiii |  | Intial temperature of the Conductor, θi | [5 empty] | : |  |  | 40 |  |  | 0C
xiv |  | Final temperature of the Conductor, θf | [5 empty] | : |  |  | 500 |  |  | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [13 empty] | {As per IS:3043-2018}
:
Where,
{As per IS:3043-2018}
[7 empty] | K |  | : |  | 80.69
|  | Cross Sectional area required, S | [5 empty] | : |  |  | 619.66 |  |  |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [6 empty] | : |  | 15 | [10 empty] | 20 x 3
|  | Cross sectional area after including allowances | [6 empty] | : |  | 712.609 |  |  |  | Sq. mm | [6 empty] | 25 x 3
25 x 6
|  | Hence Selected Strip Size | [6 empty] | : |  | 75 | X | 10 |  | Sq. mm. | [6 empty] | 25 x 8
32 x 6
32 x 10
3 |  | RESISTANCE OF GI PIPE | [19 empty] | 50 x 10
|  | Resistance of Earth Electrode is Given by | [12 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [6 empty] | 65 x 10
75 x 12
[8 empty] | = |  |  | 18.61 |  |  | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [5 empty] | = |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [5 empty] | = |  |  | 1.17 |  |  | Ω
6 |  | RESISTANCE OF EARTH STRIP | [12 empty] | {As per IS 3043-2018}
Resistance of Earth Strip is Given by
Where,
[7 empty] | t | : |  |  | Thickness of Earth Strip = 1.0 cm
[7 empty] | Rs | = |  |  | 0.43432 |  |  | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[7 empty] | RG | = |  |  | 0.31674 |  |  | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [13 empty] | {As per IS 3043-2018}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [5 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [5 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [5 empty] | = |  |  | 904.7881 |  |  | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [5 empty] | : |  |  | 0.37699 |  |  | m2
|  | Total Area of Pipe Electrode | [5 empty] | : |  |  | 6.0319 |  |  | m2
Buried Earth Strip
|  | Earth Strip Length | [5 empty] | : |  |  | 300 |  |  | m
|  | Earth Strip Width | [5 empty] | : |  |  | 0.075 |  |  | m
|  | Earth Strip Height | [5 empty] | : |  |  | 0.01 |  |  | m
|  | Total Area of Earth Strip | [5 empty] | : |  |  | 51.0015 |  |  | m2
|  | Hence Total Area of the Earthing Network (a) | [5 empty] | : |  |  | 57.0334 |  |  | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[5 empty] | Current Dissipation (I) |  |  | : |  |  | Current Density (i) * Total Area (a)
|  | I | [5 empty] | : |  |  | (A) * (B)
|  | I | [5 empty] | : |  |  | 51.6031 |  |  | kA
Maximum fault current dissipation of system is more than selected fault current of 50 kA . Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 50 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 75 x 10 mm G.I.
2. Earth Electrode selected is 40 mm dia GI. Pipe with 300 cm long
|  | 3. Total Earth Grid Resistance is |  |  |  | 0.31674 |  |  | Ω | which is less than 1 Ω.
4. Earth Electrodes:
a) For 2 Nos Transformer body Earthing - 3 Nos
b) For 2 Nos. Transformer neutral Earthing - 3 Nos
c) For Main Earth Pit - 4 Nos
d) For Body Earth Pit - 4 Nos
e) For Substation's LA Earth Pit - 3 Nos
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout.
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K

## 2 (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  | #REF! |  |  |  | DOCUMENT NO | [7 empty] | DATE
[6 empty] | #REF! | [7 empty] | #REF!
TITLE: |  | #REF! |  |  |  | DESIGNED |  |  |  | CHECKED |  |  |  | SHEET
TITLE: | [5 empty] | #REF! |  |  |  | #REF!
TYPICAL LIGHTNING PROTECTION CALCULATIONS FOR CWPH-WTP (AUL BLOCK)
I | INPUT
a | Length of the Building, L |  |  | = |  | 10 |  |  | m
b | Width of the Building, W |  |  | = |  | 10 |  |  | m
c | Height of the Building, H |  |  | = |  | 9 |  |  | m |  |  |  | {As per IEC: 62305-2: 2012}
d | Annual Thunder storm days |  |  | = |  | 50
h | Lightning flash Density per km² per Year, NG |  |  | = |  | 2.8 |  |  | /km2/yr
i | Location Factor, CD |  |  | = |  | 1
k | Reduction Factor(as a function of provisions), rp |  |  | = |  | 1
l | Reduction Factor (as a function of risk of fire), rf |  |  | = |  | 1 |  |  |  |  | {As per IEC 62305-2: 2012}
m | Special Hazard Factor, hz |  |  | = |  | 2
n | Loss Factor, LF |  |  | = |  | 2x10-2
o | Probable index for Physical Damage, PB |  |  | = |  | 1 |  |  |  |  | {As per IEC 62305-2:2012}
p | Value of Coefficient:
q | Depends on selected class of LPS, ki |  |  | = |  |  | 0.08
| Depends on electrical insulation material, km |  |  | = |  |  |  | 1 |  |  | {As per IEC 62305-3: 2011}
| Isolation of external LPS, kc |  |  | = |  |  |  | 1
r | No. of Persons in the zone, nZ
s | Total no.of persons in the structure, nt
t | Time in hours per year during which persons stay in the zone, tt | [9 empty] | {As per IEC 62305-2: 2012}
u | Loss due to Physical Damage, D2
v | Tolerable Risk, RT |  |  | = |  |  |  | 10-5 |  |  | {As per IEC 62305-2: 2012}
II | CALCULATIONS
1 | Assessment of Risk
i | Total Collection Area for a Rectangular Structure is given by, AD |  |  | = |  | (L×W)+2(3×H)*(L+W)+π(3xH)2
| AD |  |  | = |  | 3470.221 |  |  | Sq.m
ii | Probable no. of Dangerous events (Strikes) to the structure per year is given by, ND |  |  | = |  | AD x NG x CD x 10-6
| ND |  |  | = |  | 0.0097166 |  |  | Sq.m
iii | Loss due to Damage is given by, LB |  |  | = |  | rp x rf x hz x LF x (nZ / nt) x (tz / 8760)
|  |  |  | = |  | 0.04
Note :
a) When a structure is treated as a single zone the ratio nz/ nt should equate to a value of 1
b) Where the value of tz is not known, the ratio tz/8 760 should equate to a value of 1
iv | Overall Risk of Damage is given by
| Risk of Damage, R |  |  | = |  | ND x LB x PB
|  |  |  | = |  | 0.00038866
From above,
| Loss due to damage, R > Acceptable risk figure, RT (10-5). Hence, Lightning Protection is Necessary. | [10 empty] | {As per IEC: 62305-2: 2011}
2 | Electrical insulation between down conductor & near by metal parts, s |  |  | = | [8 empty] | {As per IEC: 62305-3: 2011}
|  |  |  | = |  | 0.72 |  |  | m
3 | Size of the Down Conductor (GI) |  |  |  | = | 25 x 3 |  |  | Sq.mm
III | CONCLUSION
1. Lightning calculations are done taking into consideration the Physical damage (D2)
2. Lightning protection is necessary for following Areas
a) Clear Water Pump House
b) Filter Annexe Buildinng
c) Chemical Building
d) Admin Building
3. Two down conductors are required.
4. Size of the down conductor is 25 x 3 sq. mm (GI)
Note :- |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Lightning Layout.
x kc x l
𝑘i/𝑘𝑚 x kc x l
L_B

## EP-NAVADA PS (2) (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | #REF! | [12 empty] | DOCUMENT NO | [5 empty] | DATE
[16 empty] | #REF! | [5 empty] | #REF!
TITLE: |  |  | #REF! | [12 empty] | DESIGNED |  | CHECKED |  |  |  | SHEET
TITLE: | [15 empty] | #REF! |  | #REF!
EARTHING DESIGN CALCULATIONS FOR NAVADA PS
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [10 empty] | : |  |  | 69.25 | Ohm-M |  |  | As per ERT Report
ii |  | Material of Earth Strip Selected | [10 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [10 empty] | : |  |  | GI pipe & copper Plate |  |  |  |  | As per VOLUME: II C, Technical Specs.- 4.8 Earthing and Lightning protection system and Overall Layout
iv |  | Length of cu plate | [10 empty] | : |  |  | 0.6 | m
v |  | Width of cu plate | [10 empty] | : |  |  | 0.6 | m
vi |  | Total area of plate (on both sides) | [10 empty] | : |  |  | 0.72 | m2
vii |  | Length of pipe electrode, l | [10 empty] | : |  |  | 3 | m
viii |  | Dia. of pipe electrode, d | [10 empty] | : |  |  | 40 | NB
ix |  | No. of Earth Electrodes( Plate cum Pipe ), N | [10 empty] | : |  |  | 3 | Nos.
x |  | Length of Earth Grid Strip Considered, L | [10 empty] | : |  |  | 500 | m
xi |  | Maximum Fault Current, I | [10 empty] | : |  |  | 5 | kA |  |  |  | Highest Value Considered
xii |  | Duration of Fault Current, t | [10 empty] | : |  |  | 1 | sec
xiii |  | Volumetric Heat Capacity of Conductor Material, Qc | [10 empty] | : |  |  | 0.0038 | J/0C mm3 |  |  |  | As per IS:3043-1987, Pg.no.30
xiv |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [10 empty] | : |  |  | 202 | 0C
xv |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [10 empty] | : |  |  | 0.000138 |  |  | Ohm
xvi |  | Intial temperature of the Conductor, θi | [10 empty] | : |  |  | 50 | 0C
xvii |  | Final temperature of the Conductor, θf | [10 empty] | : |  |  | 500 | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [16 empty] | {As per IS:3043-1987, Pg.no.29}
:
Where,
{As per IS:3043-1987, Pg.no.30}
[12 empty] | K |  | : |  | 79.14
|  | Cross Sectional area required, S | [10 empty] | : |  |  | 63.18 |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [11 empty] | : |  | 15
|  | Cross sectional area after including allowances | [11 empty] | : |  | 72.657 |  | Sq. mm
|  | Hence Selected Strip Size | [11 empty] | : |  | 65 X 10 |  | Sq. mm.
2 |  | RESISTANCE OF GI PLATE
|  | Resistance of Earth Electrode is Given by | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
[13 empty] | : |  |  | 36.1633 | Ω
3 |  | RESISTANCE OF GI PIPE
|  | Resistance of Earth Electrode is Given by | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
[13 empty] | : |  |  | 18.41 | Ω
4 |  | RESISTANCE OF EARTH ELECTRODE (COMBINED PIPE & PLATE ELECTRODE )
Resistance of Combined pipe & plate electrode is given by
[13 empty] | : |  |  | 12.2 | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [10 empty] | : |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [10 empty] | : |  |  | 4.07 | Ω
6 |  | RESISTANCE OF EARTH STRIP | [15 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
Resistance of Earth Strip is Given by
Where,
[12 empty] | t | : |  |  | Thickness of Earth Strip = 0.8 cm
[12 empty] | Rs | : |  |  | 0.27398 | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[13 empty] | : |  |  | 0.2567 | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [16 empty] | {As per Clause 10.3, Page No.27 of IS 3043-1987}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [10 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [10 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [10 empty] | : |  |  | 909.6744 | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Plate Electrode
|  | Area of Plate Electrode | [10 empty] | : |  |  | 0.72 | m2
|  | Total Area of Plate Electrode | [10 empty] | : |  |  | 2.16 | m2
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [10 empty] | : |  |  | 0.37699 | m2
|  | Total Area of Pipe Electrode | [10 empty] | : |  |  | 1.131 | m2
Buried Earth Strip
|  | Earth Strip Length | [10 empty] | : |  |  | 500 | m
|  | Earth Strip Width | [10 empty] | : |  |  | 0.05 | m
|  | Earth Strip Height | [10 empty] | : |  |  | 0.008 | m
|  | Total Area of Earth Strip | [10 empty] | : |  |  | 58.0008 | m2
|  | Hence Total Area of the Earthing Network (a) | [10 empty] | : |  |  | 61.2918 | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[7 empty] | Current Dissipation (I) | [5 empty] | : |  |  | Current Density (i) * Total Area (a)
|  | I | [10 empty] | : |  |  | (A) * (B)
|  | I | [10 empty] | : |  |  | 55.7556 | kA
Maximum fault current dissipation of system is more than selected fault current of 31.5 kA. Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 31.5 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 65 x 10 mm G.I.
|  | 2. Total Earth Grid Resistance is | [8 empty] | 0.2567 |  |  | Ω | which is less than 1 Ω.
|  | 3. Earth Electrode selected is . | [5 empty] | a) | 600mm x 600mm x 6 mm GI Plate for Transformer Body
[8 empty] | b) | 600 x 600 x 3.15 mm cu Plate for Transformer neutral, with 40 NB dia GI.Pipe.
As per VOLUME: II C, Technical Specs. E, M & I works, S. No.-4.8. EARTHING & LIGHTNING PROTECTION SYSTEM: Clause No. - 4.8.3( m & n )
4. Earth Electrodes:
|  |  | S. No. |  | Equipment | [5 empty] | Earth Electrode | [8 empty] | Qty
|  |  | 1 |  | Transformer body Earthing | [5 empty] | 600mm x 600mm x 6 mm GI Plate | [8 empty] | 2 Nos.
|  |  | 2 |  | Transformer neutral Earthing | [5 empty] | 600 x 600 x 3.15 mm cu Plate | [8 empty] | 2 Nos.
|  |  | 3 |  | Subatstaion & Main Earth Pits | [5 empty] | 600mm x 600mm x 6 mm GI Plate | [8 empty] | 3 Nos.
NAVADA (Switchyard)
[5 empty] | 1 | Earth Pit | [8 empty] | 4 Nos.
[5 empty] | 2 | Erath Strip | [8 empty] | 85 mtrs.
NAVADA (Pump house)
[5 empty] | 1 | Earth Pit | [8 empty] | 4 Nos.
[5 empty] | 2 | Erath Strip | [8 empty] | 530 mtrs.
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout (LE200907-E-WS-CW-DD-4011)
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_pl= ρ/4 √(/A)
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_𝑒= (𝑅_𝑝𝑙×𝑅_𝑝𝑖)/(𝑅_𝑝𝑙+𝑅_𝑝𝑖 )
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K
B
B
B

## WTP & CWPH (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: | #REF! |  | DOCUMENT NO |  | DATE
|  |  | #REF! |  | #REF!
TITLE: | ELECTRICAL EARTHING & LIGHTNING CALCULATIONS FOR WTP & CWPH |  | DESIGNED | CHECKED | SHEET
TITLE: |  |  | #REF! | #REF!
Electrical Earthing & Lightning Protection calculations For WTP & CWPH

## EP-WTP & CWPH (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  |  | #REF! | [7 empty] | DOCUMENT NO | [6 empty] | DATE
[11 empty] | #REF! | [6 empty] | #REF!
TITLE: |  |  | ELECTRICAL EARTHING CALCULATIONS FOR WTP & CWPH | [7 empty] | DESIGNED |  | CHECKED |  |  |  |  | SHEET
TITLE: | [10 empty] | #REF! |  | #REF!
EARTHING DESIGN CALCULATIONS FOR WTP & CWPH
I |  | INPUT
i |  | Average Soil Resistivity, ρ | [5 empty] | : |  |  | 65 | Ohm-M |  |  |  | Assumed |  |  | Silty clays type of soil
ii |  | Material of Earth Strip Selected | [5 empty] | : |  |  | G.I.
iii |  | Type of Earth Electrode | [5 empty] | : |  |  | GI pipe & copper Plate | [5 empty] | From GA Drawing and Overall Layout
iv |  | Length of cu plate | [5 empty] | : |  |  | 0.6 | m
v |  | Width of cu plate | [5 empty] | : |  |  | 0.6 | m
vi |  | Total area of plate (on both sides) | [5 empty] | : |  |  | 0.72 | m2
vii |  | Length of pipe electrode, l | [5 empty] | : |  |  | 3 | m
viii |  | Dia. of pipe electrode, d | [5 empty] | : |  |  | 20 | mm
ix |  | No. of Earth Electrodes( Plate cum Pipe ), N | [5 empty] | : |  |  | 3 | Nos.
x |  | Length of Earth Grid Strip Considered, L | [5 empty] | : |  |  | 300 | m
xi |  | Maximum Fault Current, I | [5 empty] | : |  |  | 35 | kA
xii |  | Duration of Fault Current, t | [5 empty] | : |  |  | 1 | sec
xiii |  | Volumetric Heat Capacity of Conductor Material, Qc | [5 empty] | : |  |  | 0.0038 | J/0C mm3 |  |  |  |  | As per IS:3043-1987, Pg.no.30
xiv |  | Reciprocal temperature coefficient of resistivity for the Conductor, B | [5 empty] | : |  |  | 202 | 0C
xv |  | Electrical Resistivity of the Conductor Material at 200°C, δ20 | [5 empty] | : |  |  | 0.000138 |  |  | Ohm
xvi |  | Intial temperature of the Conductor, θi | [5 empty] | : |  |  | 40 | 0C
xvii |  | Final temperature of the Conductor, θf | [5 empty] | : |  |  | 500 | 0C
II |  | CALCULATION
1 |  | EARTH STRIP CALCULATION
|  | Cross Sectional area of Earth strip required, S | [11 empty] | {As per IS:3043-1987, Pg.no.29}
:
Where,
{As per IS:3043-1987, Pg.no.30}
[7 empty] | K |  | : |  | 80.69
|  | Cross Sectional area required, S | [5 empty] | : |  |  | 433.76 |  | Sq. mm.
|  | Allowances in Cross-Sectional Area of the Earthing Conductor to Take the Effect of Corrosion into Account | [6 empty] | : |  | 15
|  | Cross sectional area after including allowances | [6 empty] | : |  | 498.824 |  | Sq. mm
|  | Hence Selected Strip Size | [6 empty] | : |  | 50 x 10 |  | Sq. mm.
20 x 3
2 |  | RESISTANCE OF GI PLATE | [17 empty] | 25 x 3
|  | Resistance of Earth Electrode is Given by | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [6 empty] | 25 x 6
25 x 8
32 x 6
[8 empty] | : |  |  | 33.9439 | Ω | [7 empty] | 32 x 8
3 |  | RESISTANCE OF GI PIPE | [17 empty] | 32 x 10
|  | Resistance of Earth Electrode is Given by | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987} | [6 empty] | 40 x 6
40 x 8
40 x 10
[8 empty] | : |  |  | 19.67 | Ω | [7 empty] | 50 x 6
50 x 8
4 |  | RESISTANCE OF EARTH ELECTRODE (COMBINED PIPE & PLATE ELECTRODE ) | [17 empty] | 50 x 10
65 x 10
|  |  | Resistance of Combined pipe & plate electrode is given by | [16 empty] | 75 x 12
[8 empty] | : |  |  | 12.46 | Ω
5 |  | NET RESISTANCE OF EARTH ELECTRODES
Net Resistance of Earth Electrodes is given by
|  | Rearth | [5 empty] | : |  |  | Re / N
|  | Net Resistance of Earth pits, Rearth | [5 empty] | : |  |  | 4.16 | Ω
6 |  | RESISTANCE OF EARTH STRIP | [10 empty] | {As per Amendment No.1 Jan 2006 to IS 3043-1987}
Resistance of Earth Strip is Given by
Where,
[7 empty] | t | : |  |  | Thickness of Earth Strip = 0.8 cm
[7 empty] | Rs | : |  |  | 0.41099 | Ω
7 |  | TOTAL GRID RESISTANCE
Total Grid Resistance is given by
[8 empty] | : |  |  | 0.37404 | Ω
8 | MAXIMUM PERMISSIBLE CURRENT DENSITY | MAXIMUM PERMISSIBLE CURRENT DENSITY | [11 empty] | {As per Clause 10.3, Page No.27 of IS 3043-1987}
The maximum permissible current density, i is given by
A/m2
Where,
|  | t | [5 empty] | : |  |  | Duration of the earth fault (in sec)
|  | ρ | [5 empty] | : |  |  | Resistivity of the soil (in Ω.m)
|  | Current Density (i) | [5 empty] | : |  |  | 938.9429 | A/m2 |  |  | (A)
9 |  | AREA OF THE EARTHING NETWORK
Plate Electrode
|  | Area of Plate Electrode | [5 empty] | : |  |  | 0.72 | m2
|  | Total Area of Plate Electrode | [5 empty] | : |  |  | 2.16 | m2
Pipe Electrode
|  | Area of Pipe Electrode, π x l x d | [5 empty] | : |  |  | 0.1885 | m2
|  | Total Area of Pipe Electrode | [5 empty] | : |  |  | 0.56549 | m2
Buried Earth Strip
|  | Earth Strip Length | [5 empty] | : |  |  | 300 | m
|  | Earth Strip Width | [5 empty] | : |  |  | 0.05 | m
|  | Earth Strip Height | [5 empty] | : |  |  | 0.008 | m
|  | Total Area of Earth Strip | [5 empty] | : |  |  | 34.8008 | m2
|  | Hence Total Area of the Earthing Network (a) | [5 empty] | : |  |  | 37.5263 | m2 |  |  | (B)
10 |  | MAXIMUM FAULT CURRENT DISSIPATION OF THE SYSTEM
[5 empty] | Current Dissipation (I) |  |  | : |  |  | Current Density (i) * Total Area (a)
|  | I | [5 empty] | : |  |  | (A) * (B)
|  | I | [5 empty] | : |  |  | 35.235 | kA
Maximum fault current dissipation of system is more than selected fault current of 35 kA. Hence the selected Number of Earth Electrode & Earth Strip Sizes are sufficient to dissipate fault current of 35 kA for 1Sec.
III |  | CONCLUSION
1. Main Earth Grid Conductor Selected is 50 x 10 mm G.I.
2. Earth Electrode selected is 600 x 600 x 3 mm cu. Plate with 20 mm dia GI. Pipe.
|  | 3. Total Earth Grid Resistance is |  |  |  | 0.37404 |  |  | Ω | which is less than 1 Ω.
4. Earth Electrodes:
a) For 1 Nos Transformer body Earthing - 2 Nos
b) For 1 Nos. Transformer neutral Earthing - 2 Nos
c) For 1 Nos. DG body Earthing - 2 Nos.
d) For 1 Nos. DG neutral Earthing - 2 Nos.
e) For Subatstaion & Main Earth Pits -3 Nos
Note :- |  |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Protection Layout (LE200815-E-WS-CW-DD-4012)
(I×√t)/K
K= √((Q_C (B+20))/δ_20 [ln(1+(θ_f−θ_i)/(B+θ_i ))] )
R_pl= ρ/4 √(/A)
R_𝑝𝑖= 100ρ/2π𝑙 ln 2l/𝑑
R_𝑒= (𝑅_𝑝𝑙×𝑅_𝑝𝑖)/(𝑅_𝑝𝑙+𝑅_𝑝𝑖 )
R_s= 100ρ/2πL ln 4L/t
R_G= (𝑅_𝐸𝑎𝑟𝑡ℎ×𝑅_𝑠)/(𝑅_𝐸𝑎𝑟𝑡ℎ+𝑅_𝑠 )
𝑖= (7.57 x 10^3)/√(ρ 𝑡)
(I×√t)/K

## LP-WTP & CWPH (hidden)
L&T CONSTRUCTION
WATER & EFFLUENT TREATMENT IC - EDRC
PROJECT: |  | #REF! |  |  |  |  | DOCUMENT NO | [7 empty] | DATE
[7 empty] | #REF! | [7 empty] | #REF!
TITLE: |  | ELECTRICAL LIGHTHING CALCULATIONS FOR WTP & CWPH |  |  |  |  | DESIGNED |  |  |  | CHECKED |  |  |  | SHEET
TITLE: | [6 empty] | #REF! |  |  |  | #REF!
TYPICAL LIGHTNING PROTECTION CALCULATIONS FOR WTP & CWPH
I | INPUT
a | Length of the Building, L |  |  |  | = |  | 39.3 |  |  | m
b | Width of the Building, W |  |  |  | = |  | 4.5 |  |  | m
c | Height of the Building, H |  |  |  | = |  | 9 |  |  | m |  |  |  | As per IEC: 62305-2: 2012, Pg. No.: 142 & 140
d | Annual Thunder storm days |  |  |  | = |  | 50
h | Lightning flash Density per km² per Year, NG |  |  |  | = |  | 2.8 |  |  | /km2/yr
i | Location Factor, CD |  |  |  | = |  | 1
k | Reduction Factor(as a function of provisions), rp |  |  |  | = |  | 1
l | Reduction Factor (as a function of risk of fire), rf |  |  |  | = |  | 1 |  |  |  |  | As per IEC 62305-2: 2012, Pg. No.: 50 & 51
m | Special Hazard Factor, hz |  |  |  | = |  | 2
n | Loss Factor, LF |  |  |  | = |  | 2x10-2
o | Probable index for Physical Damage, PB |  |  |  | = |  | 1 |  |  |  |  | As per IEC 62305-2:2012, Pg. No.: 41
p | Value of Coefficient:
q | Depends on selected class of LPS, ki |  |  |  | = |  |  | 0.08
| Depends on electrical insulation material, km |  |  |  | = |  |  |  | 1 |  |  | As per IEC 62305-3: 2011, Pg. No.: 36
| Isolation of external LPS, kc |  |  |  | = |  |  |  | 1
r | No. of Persons in the zone, nZ
s | Total no.of persons in the structure, nt
t | Time in hours per year during which persons stay in the zone, tt | [10 empty] | As per IEC 62305-2: 2012, Pg. No.: 51
u | Loss due to Physical Damage, D2
v | Tolerable Risk, RT |  |  |  | = |  |  |  | 10-5 |  |  | As per IEC 62305-2: 2012, Pg. No.: 22
II | CALCULATIONS
1 | Assessment of Risk
i | Total Collection Area for a Rectangular Structure is given by, AD |  |  |  | = |  | (L×W)+2(3×H)+(L+W)+π(3xH)2
| AD |  |  |  | = |  | 4832.271 |  |  | Sq.m
ii | Probable no. of Dangerous events (Strikes) to the structure per year is given by, ND |  |  |  | = |  | AD x NG x CD x 10-6
| ND |  |  |  | = |  | 0.01353 |  |  | Sq.m
iii | Loss due to Damage is given by, LB |  |  |  | = |  | rp x rf x hz x LF x (nZ / nt) x (tz / 8760)
[5 empty] | = |  | 0.04
Note :
a) When a structure is treated as a single zone the ratio nz/ nt should equate to a value of 1
b) Where the value of tz is not known, the ratio tz/8 760 should equate to a value of 1
iv | Overall Risk of Damage is given by
| Risk of Damage, R |  |  |  | = |  | ND x LB x PB
[5 empty] | = |  | 0.00054121
From above,
| Loss due to damage, R > Acceptable risk figure, RT (10-5). Hence, Lightning Protection is Necessary. | [11 empty] | As per IEC: 62305-2: 2011, Pg. No. 22
2 | Electrical insulation between down conductor & near by metal parts, s |  |  |  | = | [8 empty] | As per IEC: 62305-3: 2011, Pg. No. 38
[5 empty] | = |  | 0.72 |  |  | m
3 | Size of the Down Conductor (GI) |  |  |  |  | = | 25 x 3 |  |  | Sq.mm
III | CONCLUSION
1. Lightning calculations are done taking into consideration the Physical damage (D2)
2. Lightning protection is necessary for Filter House
3. Two down conductors are required.
4. Size of the down conductor is 25 x 3 mm (GI)
5.Lightning protection is necessary for following areas
a) Wash Water Tank Area - 2 Nos
b) Chemical House Building.- 2
c) Admin Building.- 1 No
Note :- |  | Above mentioned quantities for earth pits are minimum. However actual number of earth pits shall be as per Earthing & Lightning Layout (LE200815-E-WS-CW-DD-4012)
x kc x l
𝑘i/𝑘𝑚 x kc x l
L_B